## Fire Sprinklers Calculator
FIRE SPRINKLER CALCULATOR
EHS Tools by ORNANIT
Based on NFPA 13 2007 ed
SYSTEM DATA
| Location | Main Office
| Protected area | 5000 | ft2 |  | Ceiling height | 30 | ft
| Hazard Class | Light Hazard | Type of system |  | Wet system
| Storage Commodity | (Do not fll if ESFR) | No storage above 3.7m
| Type of storage | (Do not fll if ESFR) | No rack
| Sprinklers K (Automatic) | 5.6 | gpm/psi^0.5
| Sprinklers K (manual) | Manual Input (option) | gpm/psi^0.5
| Sprinklers K | 5.6 | gpm/psi^0.5
| Distance to water supply | 1000 | ft
| Hydraulic calculator RESULTS |  |  |  | Pipe diameter to water supply | 4 | inch
| Pressure at spr | 7 | psi
| Density | 0.1 | gpm/ft2 |  | Min spr. flow | 14.8162 | gpm
| HMD | 1500 | ft2 |  | Hose | 100 | gpm
| Required flowrate | 272.5 | gpm
| Required water supply | 272.5 | gpm @ |  | Required pressure (system) | 42.7 | psi
[5 empty] | Required pressure (supply) | 76.4703 | psi
PUMP CRITERIA
| Flow | 500 | gpm |  | Pressure | 76.4703 | psi
| Suction Dia | 5 | inch |  | Discharge | 5 | inch
| Relief valve Dia | 3 | inch |  | Relief valve discharge Dia | 5 | inch
| Meter device Dia | 5 | inch
Water supply
| Duration | 1 | Hour
| Water reservoir | 30000 | US Galons = |  | 115.5 | M3
SPRINKLERS INSTALLATION
| Max distance between spr |  | 15 | ft
| Max area covarage |  | 225 | ft2
| Max distance below ceiling |  | 12 | inch
| System Protection Area Limitations |  | 52000 | ft2
All rights reserved to Eng. A. Ornan ltd 2008 www.ornan.com
60
42
20
[5 empty] | Dencity storage | 0 |  | 28
[5 empty] | Density NO STORAGE | 0.1
[5 empty] | HMD | 1500

## Hazard Occupancies list
FIRE SPRINKLER CALCULATOR
EHS Tools by ORNANIT
Based on NFPA 13 2007 ed
HAZARD OCCUPANCIES LIST
Light Hazard occupancy
Churches
Clubs
Eaves and overhangs, if of combustible construction with no combustibles beneath
Educational
Hospitals
Institutional
Libraries, except large stack rooms
Museums
Nursing or convalescent homes
Offices, including data processing
Residential
Restaurant seating areas
Theaters and auditoriums, excluding stages and prosceniums
Unused attics
Ordinary Hazard 1
Automobile parking and showrooms
Bakeries
Beverage manufacturing
Canneries
Dairy products manufacturing and processing
Electronic plants
Glass and glass products manufacturing
Laundries
Restaurant service areas
Ordinary Hazard 2
Cereal mills
Chemical plants — ordinary
Confectionery products
Distilleries
Dry cleaners
Feed mills
Horse stables
Leather goods manufacturing
Libraries — large stack room areas
Machine shops
Metal working
Mercantile
Paper and pulp mills
Paper process plants
Piers and wharves
Post offices
Printing and publishing
Repair garages
Resin application area
Stages
Textile manufacturing
Tire manufacturing
Tobacco products manufacturing
Wood machining
Wood product assembly
Extra Hazard 1
Aircraft hangars (except as governed by NFPA 409, Standard on Aircraft Hangars)
Combustible hydraulic fluid use areas
Die casting
Metal extruding
Plywood and particle board manufacturing
Printing [using inks having flash points below 100°F (38°C)]
Rubber reclaiming, compounding, drying, milling, vulcanizing
Saw mills
Textile picking, opening, blending, garnetting, or carding, combining of cotton, synthetics, wool shoddy, or burlap
Upholstering with plastic foams
Extra Hazard 2:
Asphalt saturating
Flammable liquids spraying
Flow coating
Manufactured home or modular building assemblies (where finished enclosure is present and has combustible interiors)
Open oil quenching
Plastics processing
Solvent cleaning
Varnish and paint dipping
Pressure for ESFR K=14
Pressure for ESFR K=16.8
Pressure for ESFR K=25
#REF!
#REF!
Required pressure of spr | #REF!
#REF!

## _Options (hidden)
Light Hazard | Light Hazard | Wet system | Light Hazard | Light Hazard | Commodity I no rack | No Storage above 3.7m | Water | No storage above 3.7m | No rack
Ordinary Hazard 1 | Ordinary Hazard 1 | Dry system | Ordinary Hazard 1 | Ordinary Hazard 1 | Commodity II no rack | Commodity I no rack | Foam/Water | Commodity I | Open rack storage up to 20 ft
Ordinary Hazard 2 | Ordinary Hazard 2 | Preaction system | Ordinary Hazard 2 | Ordinary Hazard 2 | Commodity III no rack | Commodity II no rack |  | Commodity II
Extra Hazard | Extra Hazard 1 | Deluge system | Extra Hazard 1 | Extra Hazard 1 | Commodity IV no rack | Commodity III no rack |  | Commodity III
| Extra Hazard 2 |  | Extra Hazard 2 | Extra Hazard 2 | Commodity I + rack | Commodity IV no rack |  | Commodity IV
| ESFR K=14 |  | ESFR K=14 | ESFR K=14 | Commodity II + rack | Commodity I + rack
| ESFR K=16.8 |  | ESFR K=16.8 | ESFR K=16.8 | Commodity III + rack | Commodity II + rack
| ESFR K=25 |  | ESFR K=25 | ESFR K=25 | Commodity IV + rack | Commodity III + rack
|  |  | Commodity I no inrack |  |  | Commodity IV + rack
Commodity II no inrack
Commodity III no inrack
Commodity IV no inrack
Plastic A no inrack
Commodity I + inrack
Commodity II + inrack
Commodity III + inrack
Commodity IV + inrack
Plastic A + inrack
Foam/Water process plant
Foam/Water storage